## RC_SC_AT
Root Cause | Sub Cause | Action Taken
Auto Recovery | Clear_Before_Investigation | Alarm got auto clear
Auto Recovery | Clear_Before_Investigation | Sites got auto restored
Auto Recovery | Clear_Before_Investigation | Site Clear beforeFLM Reach, Auto Restored
Auto Recovery | Clear_Before_Investigation | Auto Clear Before FLM Reach
Auto Recovery | Clear_Before_Investigation | Site Clear After Weather Become Normal, Auto Clear
Auto Recovery | Clear_Before_Investigation | Site lear Before FLM Reach Auro Restored
Auto Recovery | Clear_Before_Investigation | Site Clear before FLM Reach, Auto Clear
Auto Recovery | Clear_Before_Investigation | Jeddah City have Badweather Due to Which Site Intryupted & Restored , Auto Clear
Auto Recovery | Clear_Before_Investigation | Site Clear Before FLM Reach Auto Clear , FLM Did HC & investigation
Auto Recovery | Clear_Before_Investigation | Site has Auto restored Without interference
Auto Recovery | Clear_Before_Investigation | Alarm auto cleared.
Auto Recovery | Clear_Before_Investigation | Alarm cleared
Auto Recovery | Clear_Before_Investigation | Site Clear Before FLM Reach , Auto Clear Without FLM Action
Auto Recovery | Clear_Before_Investigation | Auto Clear
Change Request RFC | Violation of Degradation Mentioned in RFC | Auto Clear
Change Request RFC | Violation of Degradation Mentioned in RFC | Violation RFC
Change Request RFC | Violation of Degradation Mentioned in RFC | Site restored after RO team has completed RFC
Change Request RFC | Violation of Degradation Mentioned in RFC | Site restored after RO team has down TS
Change Request RFC | Violation of Degradation Mentioned in RFC | Site restored,after RO team has completed RFC
Change Request RFC | Violation of Degradation Mentioned in RFC | Sites restored,after TE FLM completed RFC
Change Request RFC | Violation of Degradation Mentioned in RFC | Site restored , after RO team has completed RFC
Change Request RFC | Violation of Degradation Mentioned in RFC | Violation RFC under RO
Change Request RFC | Violation of Degradation Mentioned in RFC | Violation of Degradation Mentioned in RFC/Huaweio RO
Change Request RFC | Violation of Degradation Mentioned in RFC | Alarm Cleared
Change Request RFC | Violation of Degradation Mentioned in RFC | site was restored after NSN RO TS at site
Change Request RFC | Violation of Degradation Mentioned in RFC | RO Team working at Site Without Opening RFC and Restored after RO Team fix the issue
Change Request RFC | Violation of Degradation Mentioned in RFC | Violation of Degradation Mentioned in RFC
Change Request RFC | Violation of RFC Time | Violation RFC
Change Request RFC | Violation of RFC Time | Site restored after rfc completed (Violation of RFC Time)
Change Request RFC | Violation of RFC Time | Violation RFC under RO
Change Request RFC | Violation of RFC Time | Alarm Cleared
Change Request RFC | Violation of RFC Time | Site restored after EM FLM has completed RFC
Change Request RFC | Violation of RFC Time | Violation of RFC Time
Change Request RFC | violation_No_RFC | Violation RFC
Change Request RFC | violation_No_RFC | Salam RFC Violation
Change Request RFC | violation_No_RFC | Violation RFC under RO
Change Request RFC | violation_No_RFC | Alarm Cleared
Change Request RFC | violation_No_RFC | violation_No_RFC
Enviroment | Air Condition | Replace Indoor Power Connector
Enviroment | Air Condition | Pending on Spare
Enviroment | Air Condition | Alarm cleared after Replace Indoor Power Connector.
Enviroment | Air Condition | Reset AC
Enviroment | Air Condition | Team fix AC issue at site.
Enviroment | Air Condition | Air Condition issue
Enviroment | Air Condition | Aircon started
Enviroment | Air Condition | Alarm cleared
Enviroment | Air Condition | Change Blower
Enviroment | Air Condition | Change indoor motor
Enviroment | Air Condition | Change Outdoor motor
Enviroment | Air Condition | Welding pipes & adding freon
Enviroment | Air Condition | Welding condenser & adding Freon
Enviroment | Air Condition | Change compressor
Enviroment | Air Condition | Change Fan
Enviroment | Bill | SCECO was restored after Bill was paid by the owner
Enviroment | Circuit Breaker/Owner | Change MCCB main breaker
Enviroment | Circuit Breaker/Owner | Change MDB main breaker
Enviroment | Circuit Breaker/Owner | Change owner circuit breaker
Enviroment | Circuit Breaker/Rectifier | site down due to Faulty MDB contactor , team reached the site and replace it and site restored
Enviroment | Circuit Breaker/Rectifier | was down due to SCECO faultier , and restored after sceco restored team reached the site and found the rectefier Battery CB trip // team checked the battery status and turned on the CB
Enviroment | Circuit Breaker/Rectifier | site down due to rectifier CB trip and restored after change turned on and check all rectifier connection
Enviroment | Circuit Breaker/Rectifier | Site down due to MDB Contactor Faulty , team reached the site and replace it and site restored
Enviroment | Circuit Breaker/Rectifier | outage due to SCECO Failure / team reached the site and found the battery CB trip and site working in STB Generator
Enviroment | Circuit Breaker/Rectifier | Change rectifier main breaker
Enviroment | Circuit Breaker/Sceco | Change SCECO circuit breaker
Enviroment | Fire Alarm | Reset FACp Panel
Enviroment | Fire Alarm | Alarm cleared
Enviroment | Fire Alarm | Change smoke sensor
Enviroment | Fire Alarm | Change fire sensor
Enviroment | Fire Alarm | Change fire Pannel battery
Enviroment | Fire Alarm | Reset Fire Pannel
Enviroment | Genset failure_Alternator | Change Generator AC Alternator
Enviroment | Genset failure_Alternator | Change Generator DC Alternator
Enviroment | Genset failure_ATS | site went down due to high temp. alarm and issue resolved after team changed it and site restored
Enviroment | Genset failure_ATS | site went down due to Gen. battery for 2nd Gen. went faulty and team reached the site and fixed the DC issues and site restored
Enviroment | Genset failure_ATS | Site was down due to ATS contactor stuck, team fixed the issue and restored the site
Enviroment | Genset failure_ATS | site has dead BB and due to sceco failure site was down due to ATS problem
Enviroment | Genset failure_ATS | Due to bad weather and heavy rains, site was down due to ATS stuck , team fixed the issue and restored the site by walk as the site has damaged access road
Enviroment | Genset failure_ATS | Site down due to ATS Contactor Stuck , team reached the site and soled the issue and site restored
Enviroment | Genset failure_ATS | site has no BB and due to sceco failure site was down during the transfer to STB Generator
Enviroment | Genset failure_ATS | Site down due to ATS contactor Faulty , team reached the site and replace it and site restored
Enviroment | Genset failure_ATS | site went down due to SCECO was disconnected , STB generator not working due to ATS issue
Enviroment | Genset failure_ATS | Adjust loos power cable connection at ATS
Enviroment | Genset failure_ATS | Change ATS power cable
Enviroment | Genset failure_ATS | Change ATS relay
Enviroment | Genset failure_ATS | Change ATS contactor
Enviroment | Genset failure_AVR | Replcced AVR and restarted geneartor
Enviroment | Genset failure_AVR | Team replaced faulty AVR and restored the site
Enviroment | Genset failure_AVR | site went down due to over voltage alarm nd team fixed the issue by changed the AVR card and site restored
Enviroment | Genset failure_AVR | Site down due to AVR Card Faulty , team reached the site and replace it and site restored
Enviroment | Genset failure_AVR | Site down due to AVR Card Faulty , team replace it and site restored
Enviroment | Genset failure_AVR | site went down due to high temp. alarm and issue resolved after team changed it and site restored
Enviroment | Genset failure_AVR | Alarm cleared
Enviroment | Genset failure_AVR | Change Generator AVR
Enviroment | Genset failure_Battery charger | site restored after change Battery charger / 2nd Gen EOL not working
Enviroment | Genset failure_Battery charger | Site down due to power issue //Site located at Qaser Alouja and required permission //once access secure site restored after refilled the fuel
Enviroment | Genset failure_Battery charger | site down due to battery charger faulty ,team reached the site and replace it and site restored
Enviroment | Genset failure_Battery charger | Site down due to Battery charger fauty , team reached the site and replace it and site restored
Enviroment | Genset failure_Battery charger | Change Generator battery charger
Enviroment | Genset failure_Coolant | Alarm cleared
Enviroment | Genset failure_EFC Frequency | Site down due to under freq. alarm , team reached the site and adjust FIP and site restored
Enviroment | Genset failure_EFC Frequency | Adjust Fuel pump
Enviroment | Genset failure_EFC Frequency | Change Speed sensor
Enviroment | Genset failure_Emergency Stop | Change Generator control screen
Enviroment | Genset failure_Emergency Stop | Change Emergency stop button
Enviroment | Genset failure_Fan Belt | As per team finding that there was Genset Fan belt issue , FLM changed the Fan belt and restarted the Genset聽
Enviroment | Genset failure_Fan Belt | Change Fan Belt
Enviroment | Genset failure_Fuel | Fuel Refilled
Enviroment | Genset failure_Fuel | Alarm cleared
Enviroment | Genset failure_High Temperature | Change Radiator fan
Enviroment | Genset failure_High Temperature | Change Generator radiator
Enviroment | Genset failure_High Temperature | Change Generator water pump
Enviroment | Genset failure_Injector | site restored after FME Change Fuel Injector
Enviroment | Genset failure_Injector | Change Fuel Injector
Enviroment | Genset failure_Leakage | Change Generator oil seal due to oil leakage issue
Enviroment | Genset failure_MCU | Due to bad weather and heavy rains, Main Genset MCU and standby Genset AVR got faulty, team replaced faulty parts and restored the site by walk as the site has damaged access road
Enviroment | Genset failure_MCU | alarm cleared after adjust the MCU sitting
Enviroment | Genset failure_MCU | Alarm cleared
Enviroment | Genset failure_MCU | Change Generator controller
Enviroment | Genset failure_Oil | Site has high oil consumption as site need OH
Enviroment | Genset failure_Pressure | Change Generator speed sensor
Enviroment | Genset failure_Pressure | EOL Generator , have consumption site restored after team adjust the oil pressure
Enviroment | Genset failure_Pressure | Site down due to generator reached EOL , team reached the site and adjust oil level and site restored
Enviroment | Genset failure_Pressure | Site located at Aramco and down due to generator reached EOL , team reached the site and adjust oil level and site restored
Enviroment | Genset failure_Pressure | Alarm cleared
Enviroment | Genset failure_Pressure | Change Generator oil pressure sensor
Enviroment | Genset failure_Pump | Change Generator water pump
Enviroment | Genset failure_Pump | team change Generator Fuel pump
Enviroment | Genset failure_Pump | Change Generator fuel pump
Enviroment | Genset failure_Pump | vandalism issue BB stolen and generator stopped / 2nd generator not working due to fuel pump issue site restored after adjust the fuel pump
Enviroment | Genset failure_Pump | team repaired FIP issue and restored the site
Enviroment | Genset failure_Pump | fuel injection pump relay is faulty, and replaced
Enviroment | Genset failure_Pump | Weak BB // Change water pump injection & EOL need engine Replacement
Enviroment | Genset failure_Pump | Change Fuel Pump
Enviroment | Genset failure_Rental | Site was down due to Rental Generator under RO and was restored after RO team solved the Generator issue
Enviroment | Genset failure_Speed | generator stopped due to speed alarm and restored after adjust the fuel pump and check all fuel cycle
Enviroment | Genset failure_Speed | adjust the fuel pump and change the generator battery
Enviroment | Genset failure_Speed | Change Generator speed sensor
Enviroment | Genset failure_Starting Battery | Site was down due to faulty AVR for Main Genset and standby Genset didnt start due to starting battery vandalism, team replaced faulty AVR and starting battery and restored site
Enviroment | Genset failure_Starting Battery | Site has NO BB, it was down due to sceco failure and standby Genset didnt start due to starting battery vandalism, team installed new battery and restored the site
Enviroment | Genset failure_Starting Battery | Site was down due to sceco failure, Stand by Genset didnt start due to faulty starting battery, team replaced it and restored the site
Enviroment | Genset failure_Starting Battery | Change Generator battery
Enviroment | No Battery Bank/Dual Gen | Change Generator DC Alternator
Enviroment | No Battery Bank/Dual Gen | Site has no BB and was down during switching from SCECO to Generator
Enviroment | No Battery Bank/Dual Gen | No BB // Site down during over switch time with second power source
Enviroment | No Battery Bank/Dual Gen | down during switching fromMain Genset to Stand by Genset
Enviroment | No Battery Bank/Dual Gen | site went down during the switching bewteen both Gen. due to 1st Gen. stopped over speed alarm and Gen.2 started till the team reached the site and fixed the issue
Enviroment | No Battery Bank/Dual Gen | site went down during the switching between both Gen. as the 1st Gen. was stopped over speed alarm and site restored by 2nd Gen. till team reached the site and fixed the Gen. issue and site restored
Enviroment | No Battery Bank/Dual Gen | Site has no BB and was down during load swithcing from 1st to 2nd Generator
Enviroment | No Battery Bank/Sceco | SCECO auto restored
Enviroment | No Battery Bank/Sceco | Site down due to Sceco Failure , site restored after sceco restored
Enviroment | No Battery Bank/Sceco | No Battery Bank/and site restored after sceco restored
Enviroment | No Battery Bank/Sceco | SCECO Site ,was down due to sceco failure, restored after sceco restored
Enviroment | No Battery Bank/Sceco | Scattered sites , sies down due to No BB (No Desgin) and restored after Jamarat power restored
Enviroment | No Battery Bank/Sceco | Sites down due to No BB (no design) and restored after jamarat power restored
Enviroment | No Battery Bank/Sceco | Site was down due to sceco failure, restored after sceco restored
Enviroment | No Battery Bank/Sceco | vandalized site and power from mobily , site down due to power faailure from mobily generator , site restored after power restored
Enviroment | No Battery Bank/Sceco | Site down due sceco failure , site restored after sceco restored
Enviroment | No Battery Bank/Sceco | Vandalized site and down due to sceco failure , site restored after sceco restored
Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to SCECO failure, was restored after SCECO restored
Enviroment | No Battery Bank/Sceco | Site down due to No BB (No BB) and restored after SCECO power restored
Enviroment | No Battery Bank/Sceco | SCECO Site has NO BB, It was down due to sceco failure, restored after sceco restored
Enviroment | No Battery Bank/Sceco | site went down due to SCECO disconnected and site restored after SCECO restored
Enviroment | No Battery Bank/Sceco | site went down due to SCECO was disconnected , SCECO restored before team reached and site restored
Enviroment | No Battery Bank/Sceco | SCECO disconnected , site restored after team attend and sceco restored
Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to STC power failure, was auto restored
Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to Mobily power failure, was auto restored
Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to STC power failure, was restored after connecting PG
Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to Mobily power failure, was restored after connecting PG
Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to SCECO failure, was restored after connecting PG
Enviroment | No Battery Bank/Sceco | Site has No BB, was down due to SCECO failure, was auto restored
Enviroment | No Battery Bank/Sceco and Standby Gen | Sites were flapping during load transfer from sceco to STB GEN since sceco unstable at the area and batteries are vandalized , site restored after sceco become stable at the area
Enviroment | No Battery Bank/Sceco and Standby Gen | Site has NO BB, it was down during switching from SCECO to Stand by Genset
Enviroment | No Battery Bank/Sceco and Standby Gen | Site was down during switching from sceco to standby Genset
Enviroment | No Battery Bank/Sceco and Standby Gen | Site was down during switching from sceco to stand by genset as site has No BB
Enviroment | No Battery Bank/Sceco and Standby Gen | Site was down during switching from SCECO to stand by Genset
Enviroment | No Battery Bank/Sceco and Standby Gen | site went down during switching between SCECO and Gen. and site restored on the Gen. till SCECO restored and site restored
Enviroment | No Battery Bank/Sceco and Standby Gen | site went down during the switching bewteen SCECO and Gen. during the SCECO disconnected due to SCECO blackout as the team was facing heavy rains on that area and site restored on the GEN. TILL sceco RESTORED
Enviroment | No Battery Bank/Sceco and Standby Gen | site down due to No BB (vandalized) and restored after load transfarred from SCECO to Standby gen
Enviroment | No Battery Bank/Sceco and Standby Gen | Vandalized site and down during switching due to Sceco failure , site restored on STB generator till sceco restored
Enviroment | No Battery Bank/Sceco and Standby Gen | Site has no BB and was down during switching from SCECO to Generator
Enviroment | No Battery Bank/Single Gen | Adjust loos power cable connection at ATS
Enviroment | No Battery Bank/Single Gen | Change Emergency stop button
Enviroment | No Battery Bank/Single Gen | Change Fan Belt
Enviroment | No Battery Bank/Single Gen | Change Fuel Injector
Enviroment | No Battery Bank/Single Gen | Change Fuel Pump
Enviroment | No Battery Bank/Single Gen | Change Generator AVR
Enviroment | No Battery Bank/Single Gen | Change Generator battery
Enviroment | No Battery Bank/Single Gen | Change Generator battery charger
Enviroment | No Battery Bank/Single Gen | Change Generator controller
Enviroment | No Battery Bank/Single Gen | Change Generator oil pressure sensor
Enviroment | No Battery Bank/Single Gen | Change Generator oil seal due to oil leakage issue
Enviroment | No Battery Bank/Single Gen | Change Generator power cable
Enviroment | No Battery Bank/Single Gen | Change Generator radiator
Enviroment | No Battery Bank/Single Gen | Change Generator speed sensor
Enviroment | No Battery Bank/Single Gen | Change Generator water pump
Enviroment | No Battery Bank/Single Gen | Change Radiator fan
Enviroment | No Battery Bank/Single Gen | Change rectifer module
Enviroment | No Battery Bank/Single Gen | Change Rectifier controller
Enviroment | No Battery Bank/Single Gen | Change rectifier main breaker
Enviroment | No Battery Bank/Single Gen | Site has dead BB and site was down during switching from SCECO to Generator
Enviroment | No Battery Bank/Single Gen | Site has dead BB and was down during load swithcing from 1st to 2nd Generator
Enviroment | No Battery Bank/Single Gen | Site has high oil consumption as site need OH
Enviroment | No Battery Bank/Single Gen | Site has weak BB, team change Generator Battery
Enviroment | No Battery Bank/Single Gen | Site has weak BB, team change Generator Fuel pump
Enviroment | No Battery Bank/Single Gen | Site has weak BB, team change Generator radiator
Enviroment | No Battery Bank/Single Gen | Access road issue: Site get down due to fueling issue since access road was damaged, Team refuel the site by聽 foot and restrate generator
Enviroment | No Battery Bank/Single Gen | Site down due to high oil cinsumption as generator need major OH
Enviroment | No Battery Bank/Single Gen | Generator need OH have // change the generator oil sensor
Enviroment | No Battery Bank/Single Gen | Replcced AVR and restarted geneartor
Enviroment | No Battery Bank/Single Gen | site went dfown due to Gen. oil alarm and team fixed the issue by changed the oil sensor and site restored
Enviroment | No Battery Bank/Single Gen | Site went down due to Gen. stopped speed alarm issue and team fixed the issue and site restored
Enviroment | No Battery Bank/Single Gen | Site down due to battery charger faulty , team reached the site and replace it and site restored
Enviroment | No Battery Bank/Single Gen | Team replaced faulty oil sensor and restored the site
Enviroment | No Battery Bank/Single Gen | site went down due to Gen. stopped over speed alarm and issue fixed after team changed the fuel pump and site restored
Enviroment | No Battery Bank/Single Gen | team repaired FIP issue and restored the site
Enviroment | No Battery Bank/Single Gen | Generator need OH have // adjust the MCU sitting
Enviroment | No Battery Bank/Single Gen | Team replaced faulty AVR and restored the site
Enviroment | No Battery Bank/Single Gen | site down due to battery charger faulty ,team reached the site and replace it and site restored
Enviroment | No Battery Bank/Single Gen | alarm cleared after change Generator water Pump
Enviroment | No Battery Bank/Single Gen | Site down due to AVR Card Faulty , team replace it and site restored
Enviroment | No Battery Bank/Single Gen | site went down due to rectifier issue and site restored after team fixed the rectifier contactor
Enviroment | No Battery Bank/Single Gen | Replaced fuel relay and restarted generator
Enviroment | No Battery Bank/Single Gen | Generator stopped due to engine temperature, Replaced radiator and restarted generator
Enviroment | No Battery Bank/Single Gen | site went down due to the Gen. is EOL and have high oil consumption and team reached the site and adding the oil to the Gen. and site restored
Enviroment | No Battery Bank/Single Gen | Site down due to under freq. alarm , team reached the site and adjust FIP and site restored
Enviroment | No Battery Bank/Single Gen | Site down due to AVR Card Faulty , team reached the site and replace it and site restored
Enviroment | No Battery Bank/Single Gen | fuel injection pump relay is faulty, and replaced
Enviroment | No Battery Bank/Single Gen | Site down due to high oil cinsumption as generator need major OH ,
Enviroment | No Battery Bank/Single Gen | Generator EOL and have consumption site restored after team adjust the oil pressure
Enviroment | No Battery Bank/Single Gen | adjusted fuel injection pump
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator Battery charger / 2nd generator EOL not working
Enviroment | No Battery Bank/Single Gen | site went down due to over voltage alarm nd team fixed the issue by changed the AVR card and site restored
Enviroment | No Battery Bank/Single Gen | site went down due to Gen. stopped high temp. alarm and team fixed the issue by changed the water pump and site restorted
Enviroment | No Battery Bank/Single Gen | Replaced temprature sensor
Enviroment | No Battery Bank/Single Gen | site went down due to water pump for the Gen. went faulty and issue resolved after team changed it and site restored
Enviroment | No Battery Bank/Single Gen | site went down due to Gen. battery issue and issue resolved after the team changed the battery charger and site restored
Enviroment | No Battery Bank/Single Gen | Site down due to generator reached EOL , team reached the site and adjust oil level and site restored
Enviroment | No Battery Bank/Single Gen | site went down due to gen. Oil seal went faulty and team fixed the issue and site restored
Enviroment | No Battery Bank/Single Gen | site went down due to Gen. high temp. alarm and issue was fixed by change the water pump and site restored
Enviroment | No Battery Bank/Single Gen | site went down due to AVR card and team reached the site and fixed the issue and site restored
Enviroment | No Battery Bank/Single Gen | Generator need OH have // gesite restored after change the gen. fan belt
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator AC alternator
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator DC alternator
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator AVR
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator Water pump
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator Fuel pump
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator radiator
Enviroment | No Battery Bank/Single Gen | Site has no BB, team change Generator Battery
Enviroment | Outdoor_Temperature | Change ODC A/C controller
Enviroment | Outdoor_Temperature | Change Blower
Enviroment | Outdoor_Temperature | Change indoor motor
Enviroment | Outdoor_Temperature | Change Outdoor motor
Enviroment | Outdoor_Temperature | Welding pipes & adding freon
Enviroment | Outdoor_Temperature | Welding condenser & adding Freon
Enviroment | Outdoor_Temperature | Change compressor
Enviroment | Outdoor_Temperature | Change Fan
Enviroment | Power Cable | Chage SCECO power cable
Enviroment | Power Cable | Change Generator power cable
Enviroment | Rectifier Module | site down due to rectifier module faulty and restored after change the faulty module
Enviroment | Rectifier Module | Alarm Cleared
Enviroment | Rectifier Module | Adding module due to load issue
Enviroment | Rectifier Module | Change rectifer module
Enviroment | Rectifier_Fault | Site down due to rectifier Burnet ,restored after team fixed the issue
Enviroment | Rectifier_Fault | site down due to short circuit in rectifier backplane
Enviroment | Rectifier_Fault | site down due to cable lose in rectifier which caused overload in generator , team reached the site and fixed the issue and sites restored
Enviroment | Rectifier_Fault | site down due to short circuit in rectifier backplane , team reached the site and solved the issue and site restored
Enviroment | Rectifier_Fault | Alarm cleared
Enviroment | Rectifier_Fault | Change LVD contactor
Enviroment | Rectifier_Fault | Reset rectifier Controller
Enviroment | Rectifier_Fault | Change Rectifier controller
Enviroment | SCECO_Failure | Site has weak BB, was down due to SCECO failure, was auto restored
Enviroment | SCECO_Failure | Site was down due to SCECO failure, was auto restored
Enviroment | SCECO_Failure | Site down due to Sceco Failure , site restored on PG till sceco restored
Enviroment | SCECO_Failure | SCECO Site ,was down due to sceco failure, restored after sceco restored
Enviroment | SCECO_Failure | Site down due sceco failure , site restored after sceco restored
Enviroment | SCECO_Failure | Site was down due to sceco failure, restored after sceco restored
Enviroment | SCECO_Failure | site went down due to SCECO dissconnected and site restored after SCECO restored
Enviroment | SCECO_Failure | SCECO_Restored
Enviroment | SCECO_Failure | Sececo disconnected and rectifier battery not connected due to New Huawei rectifier MCU Stuck
Enviroment | SCECO_Failure | Site down due to Sceco Failure , and restored after team connected PG
Enviroment | SCECO_Failure | Alarm cleared after SCECO power restored
Enviroment | SCECO_Failure | SCECO Restored, Site Design Without BB
Enviroment | SCECO_Failure | sceco cut
Enviroment | SCECO_Failure | Sceco restored
Enviroment | SCECO_Failure | Alarm cleared after SCECO power restored.
Enviroment | SCECO_Failure | Alarm cleared
Enviroment | SCECO_Failure | RCA- SCECO FAILURE
Enviroment | SCECO_Failure | SCECO restored after connecting PG
Enviroment | SCECO_Failure | SCECO auto restored
Enviroment | Unauothorised Site Entrance | Door closed
Enviroment | Unauothorised Site Entrance | team reached the site and found that someone turned off the main Sceco breaker and put generator in stop mode.Power restored at site as team turned on the Sceco supply and put generator in auto mode.
Enviroment | Unauothorised Site Entrance | suspecting vandalism case, as there is door open before outage directly, and no issue observed in reporting power alarms and Genset switching.
Enviroment | Unauothorised Site Entrance | Site down due to No BB and Team reached the site and found Gen battery vandalized
Enviroment | Unauothorised Site Entrance | Unauothorised Site Entrance
Enviroment | Unauothorised Site Entrance | Unauothorised Site Entrance, door closed
Enviroment | Unauothorised Site Entrance | Alarm cleared
Enviroment | Unauothorised Site Entrance | Site was down due to unauthorized site enterance
Enviroment | Weak Battery/Dual Gen | Site has no BB and was down during load swithcing from 1st to 2nd Generator
Enviroment | Weak Battery/Dual Gen | site has Dead BB and down during switching , as main generator stopped due to AVR Card faulty
Enviroment | Weak Battery/Dual Gen | Site was down during switching from main Genset to standby Genset
Enviroment | Weak Battery/Dual Gen | Site down due to ATS Contactor faulty , team reached the site and replace it and site restored
Enviroment | Weak Battery/Dual Gen | site went down during the switching bewteen both Gen. due to 1st Gen. stopped over voltage alarm and Gen.2 started till the team reached the site and fixed the issue
Enviroment | Weak Battery/Dual Gen | Site has dead BB and was down during load swithcing from 1st to 2nd Generator
Enviroment | Weak Battery/Sceco | Site was down during bad weather in region
Enviroment | Weak Battery/Sceco | some unknown person entered & connected B2B cable in the IDU & looped the VLAN. Our team visited the site removed the B2B cable & disabled the ports after that site was cleared 鈥lease update TT owner to vandalism
Enviroment | Weak Battery/Sceco | site went down due to SCECO disconnected and site restored after SCECO restored
Enviroment | Weak Battery/Sceco | Weak BB // SCECO Restored
Enviroment | Weak Battery/Sceco | SCECO Site has dead BB, it was down due to sceco failure, restored after sceco restored
Enviroment | Weak Battery/Sceco | SCECO Site ,was down due to sceco failure, restored after sceco restored
Enviroment | Weak Battery/Sceco | Site was down due to sceco failure, restored after sceco restored
Enviroment | Weak Battery/Sceco | Site has Week BB, was down due to SCECO failure, restored after connected PG
Enviroment | Weak Battery/Sceco | Rectifier battery dead/SCECO disconnected \ Neighbors refused to allow for our team to run the PG and after discussion with him he allowed to connect it till sceco restored \ issue escalated
Enviroment | Weak Battery/Sceco | Site down due to nO BB (No design) and sceco was not availiable in hajj area, site restored after SCECO Restored
Enviroment | Weak Battery/Sceco | site power from STC and down due to power failure from STC generator , site restored after power restored
Enviroment | Weak Battery/Sceco | Rectifier battery Week /SCECO disconnected
Enviroment | Weak Battery/Sceco | site went down due to SCECO was disconnected ,team connected PG till SCECO restored
Enviroment | Weak Battery/Sceco | Site down due to NO BB (No design) and restored after SCECO Restored
Enviroment | Weak Battery/Sceco | Site has No BB, was down due to SCECO failure, was restored after SCECO restored
Enviroment | Weak Battery/Sceco | site power from Mobily and down due to power failure from mobily generator , site restored after power restored
Enviroment | Weak Battery/Sceco | SCECO Site has dead BB, Site was down due to sceco failure, restored after sceco restored
Enviroment | Weak Battery/Sceco | Site down due to No BB (No BB) and restored after SCECO power restored
Enviroment | Weak Battery/Sceco | Site down due to No BB (No BB) and power not available at site and cannot connect PG in HAJJ area , site restored after SCECO power restored
Enviroment | Weak Battery/Sceco | site has dead BB,restored after team connected PG
Enviroment | Weak Battery/Sceco | SCECO Site has weak BB, it was down due to sceco failure, restored after sceco restored
Enviroment | Weak Battery/Sceco | site went down due to SCECO was disconnected , Site restored after team reached connect the PG
Enviroment | Weak Battery/Sceco | Rectifier battery dead/SCECO disconnected
Enviroment | Weak Battery/Sceco | SCECO disconnected , site restored after team attend and sceco restored
Enviroment | Weak Battery/Sceco | site went down due to SCECO was disconnected , SCECO restored
Enviroment | Weak Battery/Sceco | site went down due to SCECO was disconnected , SCECO restored before team reached and site restored
Enviroment | Weak Battery/Sceco | Site has weak BB, was down due to STC power failure, was auto restored
Enviroment | Weak Battery/Sceco | Site has weak BB, was down due to Mobily power failure, was auto restored
Enviroment | Weak Battery/Sceco | Site has weak BB, was down due to STC power failure, was restored after connecting PG
Enviroment | Weak Battery/Sceco | Site has weak BB, was down due to Mobily power failure, was restored after connecting PG
Enviroment | Weak Battery/Sceco | Site has weak BB, was down due to SCECO failure, was restored after connecting PG
Enviroment | Weak Battery/Sceco | Site has weak BB, was down due to SCECO failure, was auto restored
Enviroment | Weak Battery/Sceco and Standby Gen | Adjust loos power cable connection at ATS
Enviroment | Weak Battery/Sceco and Standby Gen | Sites down during load transferring from sceco to STB gen as batteries are dead
Enviroment | Weak Battery/Sceco and Standby Gen | Sites were flapping during load transfer from sceco to STB GEN since sceco unstable at the area and batteries are dead, site restored after sceco become stable at the area
Enviroment | Weak Battery/Sceco and Standby Gen | site went down during the switching bewteen SCECO and Gen. and site restored by the Gen. till SCECO restored and site restored
Enviroment | Weak Battery/Sceco and Standby Gen | Site has dead BB and down during switching due to sceco failure , site restored on generatro till sceco restored
Enviroment | Weak Battery/Sceco and Standby Gen | site has dead and down due to sceco failure , site restored on STB generator till sceco restored
Enviroment | Weak Battery/Sceco and Standby Gen | Site has dead BB and site was down during switching from SCECO to Generator
Enviroment | Weak Battery/Single Gen | Change Fan Belt
Enviroment | Weak Battery/Single Gen | Change Fuel Injector
Enviroment | Weak Battery/Single Gen | Change Fuel Pump
Enviroment | Weak Battery/Single Gen | Change Generator AVR
Enviroment | Weak Battery/Single Gen | Change Generator battery charger
Enviroment | Weak Battery/Single Gen | Change Generator controller
Enviroment | Weak Battery/Single Gen | Change Generator oil pressure sensor
Enviroment | Weak Battery/Single Gen | Change Generator oil seal due to oil leakage issue
Enviroment | Weak Battery/Single Gen | Change Generator power cable
Enviroment | Weak Battery/Single Gen | Change Generator radiator
Enviroment | Weak Battery/Single Gen | Site has dead BB and was down during load swithcing from 1st to 2nd Generator
Enviroment | Weak Battery/Single Gen | Site has high oil consumption as site need OH
Enviroment | Weak Battery/Single Gen | Site has no BB, team change Generator Battery
Enviroment | Weak Battery/Single Gen | Site has no BB, team change Generator Fuel pump
Enviroment | Weak Battery/Single Gen | Site was down due to unauthorized site enterance
Enviroment | Weak Battery/Single Gen | Generator need OH consumption site restored after team adjust the oil pressure
Enviroment | Weak Battery/Single Gen | change the generator oil sensor
Enviroment | Weak Battery/Single Gen | Site down due to battery charger faulty , team reached the site and replace it and site restored
Enviroment | Weak Battery/Single Gen | Site down due to H.T Issue , team reached the site and adjust HVAC control and site restored
Enviroment | Weak Battery/Single Gen | site went down due to over voltage alarm nd team fixed the issue by changed the AVR card and site restored
Enviroment | Weak Battery/Single Gen | Team replaced fan belt and restored the site
Enviroment | Weak Battery/Single Gen | Team replaced faulty AVR and restored the site
Enviroment | Weak Battery/Single Gen | site went down due to high temp. alarm and issue resolved after team changed the water pump and site restored
Enviroment | Weak Battery/Single Gen | Bin laden securoty turned off the generator as they need to relocate the site from existing place, After negotiation with Bin laden security, we have restarted the generator.
Enviroment | Weak Battery/Single Gen | DC Alternator is faulty, and replaced
Enviroment | Weak Battery/Single Gen | Site down due to AVR Card Faulty , team replace it and site restored
Enviroment | Weak Battery/Single Gen | site went down due to high temp. alarm and issue resolved after team changed the Rediator and site restored
Enviroment | Weak Battery/Single Gen | site down due to generator High temperature sensor faulty / and restored after change it
Enviroment | Weak Battery/Single Gen | fuel injection pump relay is faulty, and replaced
Enviroment | Weak Battery/Single Gen | team reached the site and adjust oil level and site restored
Enviroment | Weak Battery/Single Gen | Site located at Aramco and down due to generator reached EOL , team reached the site and adjust oil level and site restored
Enviroment | Weak Battery/Single Gen | Site down due to generator reached EOL , team reached the site and adjust oil level and site restored
Enviroment | Weak Battery/Single Gen | generator stoped due to alternator conection problem and site restored after solve the issue
Enviroment | Weak Battery/Single Gen | Generator EOL and have consumption site restored after team adjust the oil pressure
Enviroment | Weak Battery/Single Gen | Replcced AVR and restarted geneartor
Enviroment | Weak Battery/Single Gen | Gen CB tripped and team replace it
Enviroment | Weak Battery/Single Gen | adjusted fuel injection pump
Enviroment | Weak Battery/Single Gen | Site down due to AVR Card Faulty , team reached the site and replace it and site restored
Enviroment | Weak Battery/Single Gen | Generator EOL // have high oil consumption site restored after team adjust the oil pressure
Enviroment | Weak Battery/Single Gen | FLM changed the Genset Battery charger and restarted the Genset
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator controller
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator fuel injector
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator AC alternator
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator DC alternator
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator AVR
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator Water pump
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator Fuel pump
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator radiator
Enviroment | Weak Battery/Single Gen | Site has weak BB, team change Generator Battery
LATIS Change Request | PMR Activity | PMR Activity
LATIS Change Request | BDT Activity | BDT Activity
LATIS Change Request | Installation Capex items | Installation Capex items

## Owners
Closure/ Update Owner | Escalate Owner
Building Authority | Huawei_RO
DIA | Nokia_DWDM_RO
EM phased out spare | NSN_RO
FLM_EM | BO_WIFI
Force_Majeure | BO_BSS
Fueling | BO_TRM
Huawei_MS | BO_CS
Huawei_RO | BO_PS
LATIS CR | BO_DWDM
Latis_Operation | BO_IPBB
Latis_RO | FLM_TE
LATIS_SMT | BO_IPRAN
Mobily | BO_ISP
NEC | BO_VAS
Night_Access
Nokia_DWDM_RO
NSN_RO
Pending on Spare
Relocation_RO
Salam
SCECO
Skyband
STC
TAWAL
Vandalism
ZAIN Rollout
Zain Site Management
Mobilink | In update owner only